## P6-10K Query table
| Fault code |  | warning code
Fault code or warning code (LCD): |  | 55 | Fault
Result |  | Bypass mode (standby mode or shuntdown mode) Negative power fault；To fault mode,bypass output
User behavior |  | Normal fault
Advice |  | Check whether feedback loads connected to single UPS or not;check whether feedback loads connected to parallel UPS or not,and their parallel wires are good or not.
Instruction |  | Remove all the loads, and start UPS again.
Note: 1)Fault and warning information are displayed on LCD panel, fault code has two or three numbers,warning code has three numbers. 2)Ver:0.0.1

## P10-30K Query table
Fault or warning information (LCD): | bat |  | Event
Result | Battery mode； UPS进入电池模式，历史记录显示005
User behavior | Normal working
Advice | 需结合告警内容或故障内容进行分析
Note: 1)Fault and warning information are displayed on LCD panel, or three characters displayed on history inquiry interface. 2)Some characters of fault and warning information can use "?" replace to inquire,character case insensitive. 3)Ver:0.0.1
查询表2：
请输入故障码（后台查询）： | 11 |  | #REF!
故障名称 | #REF!
触发条件 | #REF!
处理建议 | #REF!
查询表3：
请输入告警码（后台查询）： | 高 | 中 | 低
| 0 | 18 | 32768
| #REF! | #REF! | #REF!
告警名称 | #REF! | #REF! | #REF!
触发条件 |  | #REF! | #REF!
恢复条件 |  | #REF! | #REF!
处理建议 |  | #REF! | #REF!

## P6-10K Fault alarm code
序号 | Fault code / alarm code / mode code / event code | [5 empty] | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15
| bypass mode standby mode shutdown mode | main mode Frequency conversion mode | battery mode | battery selftest mode | ECO mode | history code | 中文含义 | meaning | 相关动作 | 触发条件 | 恢复条件 | 用户行为 | 故障/告警 | recommendation | Maintenance guidance
0 | 00 | 01 | 02 | 03 | 04 | X10 | BUS高压 | BUS high | To fault mode,bypass output |  | 不可恢复 | Please get in touch with nearby EAST service branches or offices | Fault | Check whether loads are half-wave loads or not, if they are, remove them,and then shutdown UPS,restart again. | 1)Remove the half-loads; 2)Check the IGBT on PFC board and INV board;
1 | 05 | 06 | 07 | 08 | 09 | X11 | BUS低压 | BUS low | To fault mode,bypass output |  | 不可恢复 | Please get in touch with nearby EAST service branches or offices | Fault | Check whether loads are half-wave loads, if they are, remove them,and then shutdown UPS,restart again. | 1)Remove the half-loads; 3)Check the IGBT on PFC board and INV board;
2 | 10 | 11 | 12 | 13 | 14 | X12 | BUS不平衡 | Bus unbalance | To fault mode,bypass output |  | 不可恢复 | Please get in touch with nearby EAST service branches or offices | Fault | Check whether loads are half-wave loads, if they are, remove them,and then shutdown UPS,restart again. | 1)Remove the half-loads; 4)Check the IGBT on PFC board and INV board;
3 | 15 | 16 | 17 | 18 | 19 | X13 | BUS软启动失败 | Bus softstart fail | To fault mode,bypass output |  | 不可恢复 | Please get in touch with nearby EAST service branches or offices | Fault | Check whether mains voltage and frequency are normal or not, or start UPS by battery,when UPS works in battery mode, switch on mains breaker,and UPS will turn to line mode. | 1)Check whether all wires connecting is normal or not; 2)Check whether input fuse and batter fuse are open or not; 3)Check the control board is good or not; 4)Maintains the PFC board according to maintenance manual.
4 | 20 | 21 | 22 | 23 | 24 | X14 | 逆变软启动失败 | Inverter softstart fail | To fault mode,bypass output |  | 不可恢复 | Please get in touch with nearby EAST service branches or offices | Fault | Check whether the wire connect PFC board and INV board is normal or not,or replace the control board and restart UPS again. | 1)Check whether all wires connecting is normal or not; 2)Replace the control board; 3)Maintains the INV board according to maintenance manual.
5 | 25 | 26 | 27 | 28 | 29 | X15 | 逆变高压 | Inverter voltage high | To fault mode,bypass output |  | 不可恢复 | Please get in touch with nearby EAST service branches or offices | Fault | Repalce the control board and check the INV board,and then start UPS again. | 1)Check whether all wires connecting is normal or not; 2)Replace the control board; 4)Maintains the INV board according to maintenance manual. | 查询内容（LCD显示） | 55 |  | 余数 | 工作模式
6 | 30 | 31 | 32 | 33 | 34 | X16 | 逆变低压 | Inverter voltage low | To fault mode,bypass output |  | 不可恢复 | Please get in touch with nearby EAST service branches or offices | Fault | Repalce the control board and check the INV board,and then start UPS again. | 1)Check whether all wires connecting is normal or not; 2)Replace the control board; 3)Maintains the INV board according to maintenance manual. | 查询内容（去掉空格） | 55 |  | 0 | Bypass mode (standby mode or shuntdown mode)
7 | 35 | 36 | 37 | 38 | 39 | X17 | BUS放电故障（未使用） | Bus discharge fail (reserved) | To fault mode,bypass output |  | 不可恢复 | Please get in touch with nearby EAST service branches or offices | Fault |  |  | 查询内容（转化为文本） | 55 |  | 1 | Line mode (Frequency conversion mode)
8 | 40 | 41 | 42 | 43 | 44 | X18 | 过温 | Over Temperature | To fault mode,bypass output |  |  | Normal fault | Fault | Check whether environment temperature is normal or not;whether the fans are normal or not;whether the air outlet is blocked by a barrier or not. | 1)Check whether the fans are normal or not; 2)Check whether the air outlet is blocked by a barrier or not,make sure the distance between rear panel and wall is larger than 1 meter; 3)Check whether environment temperature is normal or not; 4)Check whether the temperature sensors on PFC board and INV board are normal or not. | 余数 | 0 |  | 2 | Battery mode
9 | 45 | 46 | 47 | 48 | 49 | X19 | 输出短路 | Output(inverter) short | To fault mode, no bypass output |  | 不可恢复 | Please get in touch with nearby EAST service branches or offices | Fault | Check whether loads are short or not,check whether INV board output part is short or not. | 1)Remove all the loads; 2)Check whether inverter output is short circuit or not; 3)Maintains the INV board according to maintenance manual. | 取整 | 11 |  | 3 | Battery test mode
10 | 50 | 51 | 52 | 53 | 54 | X1A | 过载故障 | Overload | To fault mode, no bypass output |  | 不可恢复 | Please get in touch with nearby EAST service branches or offices | Fault | Remove non-critical devices to reduce the loads connected to UPS,and then start UPS again. | 1)Check the loads capacity; 2)Check output current sampling circuit on INV board. | 工作模式 | Bypass mode (standby mode or shuntdown mode) |  | 4 | ECO mode
11 | 55 | 56 | 57 | 58 | 59 | X1B | 负功异常 | Negative power fault | To fault mode,bypass output |  | 不可恢复 | Normal fault | Fault | Check whether feedback loads connected to single UPS or not;check whether feedback loads connected to parallel UPS or not,and their parallel wires are good or not. | Remove all the loads, and start UPS again. | 中文含义 | 负功异常
12 | 60 | 61 | 62 | 63 | 64 | X1C | 关机故障 | Shutdown fault | To fault mode,bypass output |  | 不可恢复 | Please get in touch with nearby EAST service branches or offices | Fault | Check whether SPS and control boards are normal or not. | Check whether SPS and control boards are normal or not. | 英文含义 | Negative power fault
13 | 65 | 66 | 67 | 68 | 69 | X1D | 并机软件版本不一致(未使用) | Parallel Software version conflict (reserved) | To fault mode,bypass output |  | 不可恢复 | Normal fault | Fault | Upgrade all UPS control program,and ensure the program version is the same. | Upgrade all UPS control program,and ensure the program version is the same. | 相关动作 | To fault mode,bypass output
14 | 70 | 71 | 72 | 73 | 74 | X1E | 同步信号异常(未使用) | Synchronize signal loss（reserved） | To fault mode,bypass output |  | 不可恢复 | Please get in touch with nearby EAST service branches or offices | Fault |  |  | 查询结果 | Bypass mode (standby mode or shuntdown mode) Negative power fault；To fault mode,bypass output
15 | 75 | 76 | 77 | 78 | 79 | X1F | 同步脉冲异常 | Synchronize pulse loss | To fault mode,bypass output |  | 不可恢复 | Please get in touch with nearby EAST service branches or offices | Fault | Check whether parallel wires connecting is normal or not. | 1)Check whether parallel wire is abnormal or not; 2)Check the parallel board and its wire connecting in the UPS; 3)Replace the control board. | 故障/告警 | Fault
16 | 80 | 81 | 82 | 83 | 84 | X20 | 逆变继电器粘死 | Inverter relay stuck | To fault mode,bypass output |  | 不可恢复 | Please get in touch with nearby EAST service branches or offices | Fault | Check whether the inverter relay is stuck firmly or has other abnormity or not., if it is stuck,replace it. | Replace the inverter relay. | 用户行为 | Normal fault
17 | 85 | 86 | 87 | 88 | 89 | X21 | BUS短路 | Bus short | To fault mode,bypass output |  | 不可恢复 | Please get in touch with nearby EAST service branches or offices | Fault | Check the INV board and PFC board,if they are damaged,Maintains them according to maintenance manual. | 1)Check whether line fuse,battery fuse,and inverter fuse are break or not; 2)Replace the control board; 3)Maintains the PFC and INV board according to maintenance manual. | 触发条件 | 0
18 | 90 | 91 | 92 | 93 | 94 | X22 | CAN通讯异常 | Can fault | To fault mode,bypass output |  | 不可恢复 | Please get in touch with nearby EAST service branches or offices | Fault | Check whether parallel wire is open circuit or not. | 1)Check whether parallel wire is abnormal or not; 2)Check the parallel board and its wire connecting in the UPS; 3)Replace the control board. | 恢复条件 | 不可恢复
19 | 95 | 96 | 97 | 98 | 99 | X23 | 物理地址冲突 | Parallel ID incompatible | To fault mode,bypass output |  | 不可恢复 | Please get in touch with nearby EAST service branches or offices | Fault | Check the ID of every UPS,and make sure they are different. | Reset the ID of every UPS,and make sure they are different. | 处理建议 | Check whether feedback loads connected to single UPS or not;check whether feedback loads connected to parallel UPS or not,and their parallel wires are good or not.
20 | 100 | 101 | 102 | 103 | 104 | X24 | 并机机型不兼容 | Parallel model incompatible | To fault mode, no bypass output |  | 不可恢复 | Please get in touch with nearby EAST service branches or offices | Fault | Check the type of every UPS,if they are different,repace them. | Make sure every UPS in parallel system is the same type. | 维护指导 | Remove all the loads, and start UPS again.
21 | 105 | 106 | 107 | 108 | 109 | X25 | 电池节数设置错误 | Battery number setting is wrong | To fault mode,bypass output |  | 不可恢复 | Please get in touch with nearby EAST service branches or offices | Fault | Check battery number setting. | Reset battery number. | 报错处理(0) | 1 | 1
22 | 110 | 111 | 112 | 113 | 114 | X26 | 输入SCR软启动失败 | Input SCR softstart fail | To fault mode,bypass output |  | 不可恢复 | Please get in touch with nearby EAST service branches or offices | Fault | Check whether mains voltage and frequency are normal or not;check whether the input SCR and its driver are normal or not. | 1)Check whether the input fuse is break or not; 2)Check whether the input SCR and its driver are normal or not; 3)Maintains the PFC board according to maintenance manual.
23 | 115 | 116 | 117 | 118 | 119 | X27 | 整流SCR故障(未使用) | Rectifier SCR fault（reserved） | To fault mode,bypass output |  | 不可恢复 | Please get in touch with nearby EAST service branches or offices | Fault
24 | 120 | 121 | 122 | 123 | 124 | X28 | 逆变器异常 | Inverter fault | To fault mode,bypass output |  | 不可恢复 | Please get in touch with nearby EAST service branches or offices | Fault | Check the IGBT and its driver on INV board. | 1)Replace the control board; 2)Maintains the INV board according to maintenance manual.
25 | 125 | 126 | 127 | 128 | 129 | X29 | 并机旁路接线错误 | Parallel bypass wiring is wrong | To fault mode,bypass output |  | 不可恢复 | Please get in touch with nearby EAST service branches or offices | Fault | Check whether bypass sequence of every parallel UPS is the same or not. | Check whether bypass sequence of every parallel UPS is the same or not.
26 | 130 | 131 | 132 | 133 | 134 | X2A | 逆变保险熔断 | Inverter fuse break | To fault mode,bypass output |  | 不可恢复 | Please get in touch with nearby EAST service branches or offices | Fault | Check whether the inverter output fuse is good or not,if its bad, Replace it,and then start UPS step by step. | Check whether the inverter output fuse is good or not,if its bad, Replace it,and then start UPS step by step.
27 | 135 | 136 | 137 | 138 | 139 | X2B | PFC异常 | PFC fault | To fault mode,bypass output |  | 不可恢复 | Please get in touch with nearby EAST service branches or offices | Fault | Check whether input fuse and battery fuse are break or not. | 1)Check whether input fuse and battery fuse are break or not; 2)Check PFC current sampling circuit; 3)Maintains the PFC board according to maintenance manual.
28 | 140 | 141 | 142 | 143 | 144 | X2C | 逆变电容异常 | Inverter capacitor fault | To fault mode,bypass output |  | 不可恢复 | Please get in touch with nearby EAST service branches or offices | Fault | Check whether the inverter output filter capacitor is good or not,if it is bad,replace it. | Check whether the inverter output filter capacitor is good or not,if it is bad,replace it.
29 | 145 | 146 | 147 | 148 | 149 | X2D | 风扇故障 | Fan fail | To fault mode,bypass output |  | 不可恢复 | Please get in touch with nearby EAST service branches or offices | Fault | Check whether the fan is connected well or not; Check whether the fan is blocked and damaged or not. | 1)Check whether the fan is blocked or not; 2)Check whether the fan wire connecting and terminal are good or not; 3)Replace the control board.
30 | 150 | 151 | 152 | 153 | 154 | X2E | EPO | Emergency power off | To fault mode,bypass output |  | 不可恢复 | Normal fault | Fault | Check EPO wire. | 1)Check EPO wire; 2)Replace the control board.
31 | 155 | 156 | 157 | 158 | 159 | X2F | 7: 本组故障码未使用; 8: reserved; 10: 此故障码未使用; 11: 此故障码未使用; 13: Fault
32 | 160 | 161 | 162 | 163 | 164 | X30 | 7: 本组故障码未使用; 8: reserved; 10: 此故障码未使用; 11: 此故障码未使用; 13: Fault
33 | 165 | 166 | 167 | 168 | 169 | X31 | 7: 本组故障码未使用; 8: reserved; 10: 此故障码未使用; 11: 此故障码未使用; 13: Fault
34 | 170 | 171 | 172 | 173 | 174 | X32 | 7: 本组故障码未使用; 8: reserved; 10: 此故障码未使用; 11: 此故障码未使用; 13: Fault
35 | 175 | 176 | 177 | 178 | 179 | X33 | 7: 本组故障码未使用; 8: reserved; 10: 此故障码未使用; 11: 此故障码未使用; 13: Fault
36 | 180 | 181 | 182 | 183 | 184 | X34 | 7: 本组故障码未使用; 8: reserved; 10: 此故障码未使用; 11: 此故障码未使用; 13: Fault
37 | 185 | 186 | 187 | 188 | 189 | X35 | 7: 本组故障码未使用; 8: reserved; 10: 此故障码未使用; 11: 此故障码未使用; 13: Fault
38 | 190 | 191 | 192 | 193 | 194 | X36 | 7: 本组故障码未使用; 8: reserved; 10: 此故障码未使用; 11: 此故障码未使用; 13: Fault
39 | 195 | 196 | 197 | 198 | 199 | X37 | 7: 本组故障码未使用; 8: reserved; 10: 此故障码未使用; 11: 此故障码未使用; 13: Fault
40 | 200 | 0x0001 | 第16位告警 |  |  | X40 | 7: 此告警码未使用; 8: reserved; 12: Normal alarm; 13: Warning
41 | 201 | 0x0002 |  |  |  | X41 | 并机设置错误 | Parallel Set Fail | Startup forbidden |  |  | Normal alarm | Warning | For single UPS,set PAL off; for parallel UPS,set PAL on and connect the communication wire.
42 | 202 | 0x0004 |  |  |  | X42 | 7: 此告警码未使用; 8: reserved; 12: Normal alarm; 13: Warning
43 | 203 | 0x0008 |  |  |  | x43 | 过载告警 | Overload warning | Overload time over,to bypass mode,time over again,to fault mode,no bypass output. |  |  | Normal alarm | Warning | Remove non-critical devices to reduce the loads connected to UPS.
44 | 204 | 0x0010 |  |  |  | X44 | 电池未接 | Battery disconnect | Shutdown charger |  |  | Normal alarm | Warning | Connect battery and switch on battery breaker.
45 | 205 | 0x0020 |  |  |  | X45 | 过充 | Over charge | Shutdown charger |  |  | Normal alarm | Warning | Switch off battery breaker, remove devices connected to UPS, shutdown UPS, and replace new charger.
46 | 206 | 0x0040 |  |  |  | X46 | 7: 此告警码未使用; 8: reserved; 12: Normal alarm; 13: Warning
47 | 207 | 0x0080 |  |  |  | X47 | 开机异常 | UPS startup fail | Cancel startup |  |  | Normal alarm | Warning | Connect normal mains (normal voltage and normal frequency), restart up UPS.
48 | 208 | 0x0100 |  |  |  | X48 | 充电器故障 | Charger fail | Shutdown charger |  |  | Normal alarm | Warning | Switch off battery breaker, remove devices connected to UPS, shutdown UPS, and replace the charger.
49 | 209 | 0x0200 |  |  |  | X49 | EEPROM异常 | EEPROM Read/Write fail | Program judges parameters are nomal or not,if they are normal,parameters keep on,if they are abnormal,the paremeters auto reset. |  |  | Normal alarm | Warning | Clean the warning by LCD panel or using debug software. Or shutdown UPS and startup again.
50 | 210 | 0x0400 |  |  |  | X4A | 7: 此告警码未使用; 8: reserved; 12: Normal alarm; 13: Warning
51 | 211 | 0x0800 |  |  |  | X4B | 电池低压 | Battery low | Warning! battery capacity is very low! And UPS will shutdown or turn to bypass mode. |  |  | Normal alarm | Warning | Remove non-critical devices and charge the battery as soon as possible.
52 | 212 | 0x1000 |  |  |  | X4C | AD采样异常 | AD sample fail | Keep in power on mode |  |  | Normal alarm | Warning | Replace the control board.
53 | 213 | 0x2000 |  |  |  | X4D | 同步脉冲异常 | Synchronize pulse loss | Host and guest UPS both warn, and keep in current working mode. |  |  | Normal alarm | Warning | Check the parallel wire connecting and parallel board are abnormal or not.
54 | 214 | 0x4000 |  |  |  | X4E | 同步信号异常 | Synchronize signal loss | Guest UPS output cutoff,host UPS keep in current mode,and startup forbidden. |  |  | Normal alarm | Warning | Check the parallel wire connecting and parallel board are abnormal or not.
55 | 215 | 0x8000 |  |  |  | X4F | 7: CAN通讯异常; 8: CAN Communication fail; 12: Normal alarm; 13: Warning; 14: Check the parallel wire connecting and parallel board are abnormal or not.
56 | 216 | 0x0001 | 中16位告警 |  |  | X50 | 旁路高压 | Bypass voltage is high | Do not allowed turning to bypass. |  |  | Normal alarm | Warning | Check bypass voltage is normal or not.
57 | 217 | 0x0002 |  |  |  | X51 | 旁路超高压 | Bypass voltage is extremely high | Do not allowed turning to bypass. |  |  | Normal alarm | Warning | Check bypass voltage is normal or not.
58 | 218 | 0x0004 |  |  |  | X52 | 市电高压 | Mains voltage is high | To battery mode |  |  | Normal alarm | Warning | Check mains voltage is normal or not.
59 | 219 | 0x0008 |  |  |  | X53 | 市电频率异常 | Mains frequency is abnormal | To battery mode |  |  | Normal alarm | Warning | Check mains frequency is normal or not.
60 | 220 | 0x0010 |  |  |  | X54 | 7: 旁路市电相序不一致(未使用); 8: mains and bypass reverse sequence(reserved); 9: Startup forbidden; 12: Normal alarm; 13: Warning
61 | 221 | 0x0020 |  |  |  | X55 | 7: 此告警码未使用; 8: reserved; 12: Normal alarm; 13: Warning
62 | 222 | 0x0040 |  |  |  | X56 | 电池放电终止 | End Of Discharge | To standby mode or bypass mode |  |  | Normal alarm | Warning | Charge the battery as soon as possible.
63 | 223 | 0x0080 |  |  |  | X57 | 逆变电容异常 | Inverter capacitor is abnormal | Warning! Inverter capacitor is abnormal, replace it immediately! |  |  | Normal alarm | Warning | Check whether the filter capacitor of inverter is abnormal or not.
64 | 224 | 0x0100 |  |  |  | X58 | 禁止开机 | Forbid to start UPS | Startup forbidden |  |  | Normal alarm | Warning | Check mains voltage and frequency,battery voltage is normal or not.
65 | 225 | 0x0200 |  |  |  | X59 | 7: 此告警码未使用; 8: reserved; 12: Normal alarm; 13: Warning
66 | 226 | 0x0400 |  |  |  | X5A | 7: 此告警码未使用; 8: reserved; 12: Normal alarm; 13: Warning
67 | 227 | 0x0800 |  |  |  | X5B | 7: 此告警码未使用; 8: reserved; 12: Normal alarm; 13: Warning
68 | 228 | 0x1000 |  |  |  | X5C | 7: 此告警码未使用; 8: reserved; 12: Normal alarm; 13: Warning
69 | 229 | 0x2000 |  |  |  | X5D | 7: 此告警码未使用; 8: reserved; 12: Normal alarm; 13: Warning
70 | 230 | 0x4000 |  |  |  | X5E | 7: 此告警码未使用; 8: reserved; 12: Normal alarm; 13: Warning
71 | 231 | 0x8000 |  |  |  | X5F | 7: 此告警码未使用; 8: reserved; 12: Normal alarm; 13: Warning
72 | 232 | 0x0001 | 高16位告警 |  |  | X60 | PFC异常 | PFC current is abnormal | Warning! |  |  | Normal alarm | Warning | Shutdown UPS, check the input fuse and battery fuse.
73 | 233 | 0x0002 |  |  |  | X61 | 7: 此告警码未使用; 8: reserved; 12: Normal alarm; 13: Warning
74 | 234 | 0x0004 |  |  |  | X62 | 市电异常（市电波形异常或市电低压） | Mains is abnormal | To batery mode or standby mode. |  |  | Normal alarm | Warning | Check mains voltage and frequency is normal or not.
75 | 235 | 0x0008 |  |  |  | X63 | 旁路异常（旁路波形异常或旁路低压） | Bypass is abnormal | To bypass mode forbidden |  |  | Normal alarm | Warning | Check bypass voltage and frequency is normal or not.
76 | 236 | 0x0010 |  |  |  | X64 | 旁路频率异常 | Bypass frequency is abnormal | To bypass mode forbidden |  |  | Normal alarm | Warning | Check bypass frequency is normal or not.
77 | 237 | 0x0020 |  |  |  | X65 | 7: 输出电压侦测异常（未使用）; 8: Output voltage is abnormal(reserved); 12: Normal alarm; 13: Warning
78 | 238 | 0x0040 |  |  |  | X66 | 7: 电池电压异常（未使用）; 8: Battery voltage is abnormal(reserved); 9: Startup forbidden; 12: Normal alarm; 13: Warning
79 | 239 | 0x0080 |  |  |  | X67 | ECO不稳定 | ECO instable | Forbid entering in ECO mode |  |  | Normal alarm | Warning | Clean the warning by LCD panel or using debug software. When mains and bypass are normal, set ECO enable.
80 | 240 | 0x0100 |  |  |  | X68 | 7: 负载不稳定（未使用）; 8: Load unstable(reserved); 9: Forbid startup inverter.; 12: Normal alarm; 13: Warning
81 | 241 | 0x0200 |  |  |  | X6A | 维修旁路使能 | Maintenance bypass breaker open | To bypass mode,startup forbidden. |  |  | Normal alarm | Warning | Fix the maintenance bypass baffle.
82 | 242 | 0x0400 |  |  |  | X69 | 过温频繁 | Over Temperature often | Keeping in bypass mode, do not startup again. |  |  | Normal alarm | Warning | Clean the warning by LCD panel or using debug software, or start UPS to clean the warning. (Insure to find the reason of over temperature)
83 | 243 | 0x0800 |  |  |  | X6B | 并机电池节数设置不一致 | Parallel Bat Num is wrong | Startup forbidden |  |  | Normal alarm | Warning | Set battery number by LCD panel again.
84 | 244 | 0x1000 |  |  |  | X6C | 7: 电池温度补偿异常（未使用）; 8: Battery temperature compensation is abnormal(reserved); 9: Shutdown charger; 12: Normal alarm; 13: Warning
85 | 245 | 0x2000 |  |  |  | X6D | 7: 旁路电压不稳定(未使用); 8: Bypass voltage instable(reserved); 12: Normal alarm; 13: Warning
86 | 246 | 0x4000 |  |  |  | X6E | 测试模式 | Test mode | UPS working in debug mode. |  |  | Normal alarm | Warning | You can cancel TEST MODE using debug software.
87 | 247 | 0x8000 |  |  |  | X6F | 过载频繁 | Overload Often | Keeping in bypass mode, do not startup again. |  |  | Normal alarm | Warning | Clean the warning by LCD panel or using debug software, or start UPS to clean the warning. (Insure to find the reason of overload.)
| 以下为模式码： |  |  |  |  | 以下为模式码：
88 | 0 |  |  |  |  | 00 | 7: 故障告警消除; 8: Faults and warnings Dispelled; 10: 故障告警条件消除; 11: 故障告警条件发生
89 | 1 |  |  |  |  | 01 | 7: 上电模式; 8: Power on mode; 9: UPS进入上电模式，历史记录显示001; 14: UPS首次通电点亮屏幕，是UPS开始运行的标志
90 | 2 |  |  |  |  | 02 | 7: 待机模式; 8: Standby mode; 9: UPS进入待机模式，历史记录显示002; 14: 需结合告警内容或故障内容进行分析
91 | 3 |  |  |  |  | 03 | 7: 旁路模式; 8: Bypass mode; 9: UPS进入旁路模式，历史记录显示003; 14: 需结合告警内容或故障内容进行分析
92 | 4 |  |  |  |  | 04 | 7: 市电模式; 8: Line mode; 9: UPS进入市电模式，历史记录显示004; 14: 需结合告警内容或故障内容进行分析
93 | 5 |  |  |  |  | 05 | 7: 电池模式; 8: Battery mode; 9: UPS进入电池模式，历史记录显示005; 14: 需结合告警内容或故障内容进行分析
94 | 6 |  |  |  |  | 06 | 7: 电池自检模式; 8: Battery test mode; 9: UPS进入电池自检模式，历史记录显示006; 14: 需结合告警内容或故障内容进行分析
95 | 7 |  |  |  |  | 07 | 7: 故障模式; 8: Fault mode; 9: UPS进入故障模式，历史记录显示007; 14: 需结合告警内容或故障内容进行分析
96 | 8 |  |  |  |  | 08 | 7: 变频模式; 8: Frequency conversion mode; 9: UPS进入变频模式，历史记录显示008; 14: 需结合告警内容或故障内容进行分析
97 | 9 |  |  |  |  | 09 | 7: 经济运行模式; 8: ECO mode; 9: UPS进入ECO模式，历史记录显示009; 14: 需结合告警内容或故障内容进行分析
98 | A |  |  |  |  | 0A | 7: 关机模式; 8: Shutdown mode; 9: UPS进入关机模式，历史记录显示00A; 14: 控制板发的关机信号，需确认是手动关机还是EOD导致的
99 | B |  |  |  |  | 0B | 7: 测试模式; 8: Test mode; 9: UPS进入测试模式，历史记录显示00B; 14: 调试完成后可关闭此模式即进入正常工作模式
100 | C |  |  |  |  | 0C | bar: 7 to 15
101 | D |  |  |  |  | 0D | bar: 7 to 15
102 | E |  |  |  |  | 0E | bar: 7 to 15
103 | F |  |  |  |  | 0F | bar: 7 to 15
| 以下为事件码： |  |  |  |  | 以下为事件码：
104 | [5 empty] | X80 | 7: Bus 软启动; 8: Bus softstar
105 | [5 empty] | X81 | 7: 逆变软启动; 8: Inverter softstart
106 | [5 empty] | X82 | 7: 输入SCR软启动; 8: IPSCR softstart
107 | [5 empty] | X83 | 7: 输入SCR快速启动; 8: Fast IPSCR softstart
108 | [5 empty] | X84 | 7: UPS关机; 8: UPS Off
109 | [5 empty] | X85 | 7: UPS开机; 8: UPS On
110 | [5 empty] | X86 | 7: 充电器开启; 8: Charger On
111 | [5 empty] | X87 | 7: 充电器关闭; 8: Charger Off
112 | [5 empty] | X88 | 7: 充电器均充; 8: Average Charge
113 | [5 empty] | X89 | 7: 充电器浮充; 8: Float Charge
114 | [5 empty] | X8A | 7: 充电器休眠; 8: Dormant Charger
115 | [5 empty] | X8B | 7: 充电器待机; 8: Reset Charger
116 | [5 empty] | X8C | 7: 自动重启; 8: Auto start
117 | [5 empty] | X8D | bar: 7 to 8
118 | [5 empty] | X8E | bar: 7 to 8
119 | [5 empty] | X8F | bar: 7 to 8

## P10-30K History (LCD query)
EA900P 10-30kVA(3/3)历史记录及分析
LCD模式栏/状态栏 显示内容 | LCD模式栏/状态栏 显示内容(去掉空格） | 模式码/故障码/告警码/事件码（X为模式码，从1-F，共15个） |  | 英文含义 | 中文含义 | 触发条件 | 恢复条件 | 相关动作 | 问题排查及解决方法 | 用户行为 | 故障/告警/事件 | 维护指导
以下为工作模式信息：
|  | 0 | 00 | Faults and warnings Dispelled | 故障告警消除 | 故障告警条件消除 | 故障告警条件发生 |  |  | Normal working | Event
10KUA/ 15KUA/ 20KUA/ 30KUA | 10KUA/ 15KUA/ 20KUA/ 30KUA | 1 | 01 | Power on mode | 上电模式 |  |  | UPS进入上电模式，历史记录显示001 | UPS首次通电点亮屏幕，是UPS开始运行的标志 | Normal working | Event |  | 用户行为 |  | Normal working
STdby | STdby | 2 | 02 | Standby mode | 待机模式 |  |  | UPS进入待机模式，历史记录显示002 | 需结合告警内容或故障内容进行分析 | Normal working | Event |  | 维护指导
byPASS | byPASS | 3 | 03 | Bypass mode | 旁路模式 |  |  | UPS进入旁路模式，历史记录显示003 | 需结合告警内容或故障内容进行分析 | Normal working | Event
LInE | LInE | 4 | 04 | Line mode | 市电模式 |  |  | UPS进入市电模式，历史记录显示004 | 需结合告警内容或故障内容进行分析 | Normal working | Event
bAT | bAT | 5 | 05 | Battery mode | 电池模式 |  |  | UPS进入电池模式，历史记录显示005 | 需结合告警内容或故障内容进行分析 | Normal working | Event |  | 查询内容（状态栏显示内容） | bat
bATT | bATT | 6 | 06 | Battery test mode | 电池自检模式 |  |  | UPS进入电池自检模式，历史记录显示006 | 需结合告警内容或故障内容进行分析 | Normal working | Event |  | 查询内容（去掉空格） | bat
FAULT | FAULT | 7 | 07 | Fault mode | 故障模式 |  |  | UPS进入故障模式，历史记录显示007 | 需结合告警内容或故障内容进行分析 | Normal working | Event |  | 英文含义（查询结果） | Battery mode | Battery mode； UPS进入电池模式，历史记录显示005
CUCF | CUCF | 8 | 08 | Converter mode | 变频模式 |  |  | UPS进入变频模式，历史记录显示008 | 需结合告警内容或故障内容进行分析 | Normal working | Event |  | 中文含义（查询结果） |  | 电池模式； UPS进入电池模式，历史记录显示005
ECO | ECO | 9 | 09 | ECO mode | 经济运行模式 |  |  | UPS进入ECO模式，历史记录显示009 | 需结合告警内容或故障内容进行分析 | Normal working | Event |  | 触发条件
SHUTdn | SHUTdn | A | 0A | Shutdown mode | 关机模式 |  |  | UPS进入关机模式，历史记录显示00A | 控制板发的关机信号，需确认是手动关机还是EOD导致的 | Normal working | Event |  | 恢复条件
TEST | TEST | B | 0B | Test mode | 测试模式 |  |  | UPS进入测试模式，历史记录显示00B | 可通过后台软件关闭测试模式 | Normal working | Event |  | 相关动作 |  | UPS进入电池模式，历史记录显示005
保留 | 保留 | C | 0C | reserved | 保留 | 未使用 | 未使用 | 未使用 | 未使用 | Normal working | Event |  | 处理建议 |  | 需结合告警内容或故障内容进行分析
保留 | 保留 | D | 0D | reserved | 保留 | 未使用 | 未使用 | 未使用 | 未使用 | Normal working | Event
保留 | 保留 | E | 0E | reserved | 保留 | 未使用 | 未使用 | 未使用 | 未使用 | Normal working | Event |  | 报错处理 | Battery mode | Battery mode | 1 | Event
保留 | 保留 | F | 0F | reserved | 保留 | 未使用 | 未使用 | 未使用 | 未使用 | Normal working | Event
以下为故障信息（现象为蜂鸣器长鸣,故障灯红灯常亮）： | [12 empty] | 字符个数 | 3
bUS HIgH | bUSHIgH | X10 | 10 | Bus voltage is high | BUS高压 |  | 不可恢复 | To fault mode,bypass output | Check whether loads are half-wave loads or not, if they are, remove them,and then shutdown UPS,restart again. | Normal fault | Fault | 1)Remove the half-loads; 2)Check the IGBT on PFC board and INV board; | 查询内容为分解 | b | a | t | at
bUS LOW | bUSLOW | X11 | 11 | Bus voltage is low | BUS低压 |  | 不可恢复 | To fault mode,bypass output | Check whether loads are half-wave loads, if they are, remove them,and then shutdown UPS,restart again. | Normal fault | Fault | 1)Remove the half-loads; 3)Check the IGBT on PFC board and INV board; | 转化为大写 | B | A | T | AT
bUS UnbAL | bUSUnbAL | X12 | 12 | Bus voltage is unbalance | BUS不平衡 |  | 不可恢复 | To fault mode,bypass output | Check whether loads are half-wave loads, if they are, remove them,and then shutdown UPS,restart again. | Normal fault | Fault | 1)Remove the half-loads; 4)Check the IGBT on PFC board and INV board; | 查询内容为编码(1) | 0
bUSSOFT F | bUSSOFTF | X13 | 13 | Bus softstart fail | BUS软启动失败 |  | 不可恢复 | To fault mode,bypass output | Check whether mains voltage and frequency are normal or not, or Start UPS by battery,when UPS works in battery mode, switch on mains breaker,and UPS will turn to line mode. | Please get in touch with nearby EAST service branches or offices | Fault | 1)Check whether all wires connecting is normal or not; 2)Check whether input fuse and batter fuse are open or not; 3)Check the control board is good or not; 4)Maintains the PFC board according to maintenance manual. | 编码查询出错 | 0 | 0 | 0 | 0
bUS SHORT | bUSSHORT | X14 | 14 | Bus shorted | BUS短路 |  | 不可恢复 | To fault mode,bypass output | Check the INV board and PFC board,if they are damaged,Maintains them according to maintenance manual. | Please get in touch with nearby EAST service branches or offices | Fault | 1)Check whether line fuse,battery fuse,and inverter fuse are break or not; 2)Replace the control board; 3)Maintains the PFC and INV board according to maintenance manual.
bUSdISC F | bUSdISCF | X15 | 15 | Bus discharging fail（reserved） | BUS放电故障(未使用) |  | 不可恢复 | To fault mode,bypass output |  | Please get in touch with nearby EAST service branches or offices | Fault
InU HIgH | InUHIgH | X16 | 16 | Inverter voltage is high | 逆变高压 |  | 不可恢复 | To fault mode,bypass output | Repalce the control board and check the INV board,and then Start UPS again. | Please get in touch with nearby EAST service branches or offices | Fault | 1)Check whether all wires connecting is normal or not; 2)Replace the control board; 4)Maintains the INV board according to maintenance manual.
InU LOW | InULOW | X17 | 17 | Inverter voltage is low | 逆变低压 |  | 不可恢复 | To fault mode,bypass output | Repalce the control board and check the INV board,and then Start UPS again. | Please get in touch with nearby EAST service branches or offices | Fault | 1)Check whether all wires connecting is normal or not; 2)Replace the control board; 5)Maintains the INV board according to maintenance manual.
InUSOFT F | InUSOFTF | X18 | 18 | Inverter sotstart fail | 逆变软启动失败 |  | 不可恢复 | To fault mode,bypass output | Check whether the wire connect PFC board and INV board is normal or not,or replace the control board and restart UPS again. | Please get in touch with nearby EAST service branches or offices | Fault | 1)Check whether all wires connecting is normal or not; 2)Replace the control board; 6)Maintains the INV board according to maintenance manual.
AOP SHORT | AOPSHORT | X19 | 19 | A Phase Output short circuited | A相相电压短路 |  | 不可恢复 | To fault mode, no bypass output | Check whether loads connected A phase are short or not,check whether A phase INV board output part is short or not. | Please get in touch with nearby EAST service branches or offices | Fault | 1)Remove all the loads; 2)Check whether inverter output is short circuit or not; 3)Maintains A phase INV board according to maintenance manual.
BOP SHORT | BOPSHORT | X1A | 1A | B Phase Output short circuited | B相相电压短路 |  | 不可恢复 | To fault mode, no bypass output | Check whether loads connected B phase are short or not,check whether B phase INV board output part is short or not. | Please get in touch with nearby EAST service branches or offices | Fault | 1)Remove all the loads; 2)Check whether inverter output is short circuit or not; 4)Maintains B phase INV board according to maintenance manual.
COP SHORT | COPSHORT | X1B | 1B | C Phase Output short circuited | C相相电压短路 |  | 不可恢复 | To fault mode, no bypass output | Check whether loads connected C phase are short or not,check whether C phase INV board output part is short or not. | Please get in touch with nearby EAST service branches or offices | Fault | 1)Remove all the loads; 2)Check whether inverter output is short circuit or not; 5)Maintains C phase INV board according to maintenance manual.
AB SHORT | ABSHORT | X1C | 1C | AB Phase Output short circuited | AB线电压短路 |  | 不可恢复 | To fault mode, no bypass output | Check whether loads connected A and B phase are short or not,check whether A and B phase INV board output part is short or not. | Please get in touch with nearby EAST service branches or offices | Fault | 1)Remove all the loads; 2)Check whether inverter output is short circuit or not; 6)Maintains A and B phase INV board according to maintenance manual.
BC SHORT | BCSHORT | X1D | 1D | BC Phase Output short circuited | BC线电压短路 |  | 不可恢复 | To fault mode, no bypass output | Check whether loads connected B and C phase are short or not,check whether B and C phase INV board output part is short or not. | Please get in touch with nearby EAST service branches or offices | Fault | 1)Remove all the loads; 2)Check whether inverter output is short circuit or not; 7)Maintains B and C phase INV board according to maintenance manual.
CA SHORT | CASHORT | X1E | 1E | CA Phase Output short circuited | CA线电压短路 |  | 不可恢复 | To fault mode, no bypass output | Check whether loads connected C and A phase are short or not,check whether C and A phase INV board output part is short or not. | Please get in touch with nearby EAST service branches or offices | Fault | 1)Remove all the loads; 2)Check whether inverter output is short circuit or not; 8)Maintains C and A phase INV board according to maintenance manual.
AnEgPOW F | AnEgPOWF | X1F | 1F | A Phase Negative power Fault | A相负功异常 |  | 不可恢复 | To fault mode,bypass output | Check whether feedback loads connected to single UPS or not;check whether feedback loads connected to parallel UPS or not,and their parallel wires are good or not. | Normal fault | Fault | Remove all the loads, and Start UPS again.
BnEgPOW F | BnEgPOWF | X20 | 20 | B Phase Negative power Fault | B相负功异常 |  | 不可恢复 | To fault mode,bypass output | Check whether feedback loads connected to single UPS or not;check whether feedback loads connected to parallel UPS or not,and their parallel wires are good or not. | Normal fault | Fault | Remove all the loads, and Start UPS again.
CnEgPOW F | CnEgPOWF | X21 | 21 | C Phase Negative power Fault | C相负功异常 |  | 不可恢复 | To fault mode,bypass output | Check whether feedback loads connected to single UPS or not;check whether feedback loads connected to parallel UPS or not,and their parallel wires are good or not. | Normal fault | Fault | Remove all the loads, and Start UPS again.
INVRLY F | INVRLYF | X22 | 22 | Inverter relay short | 逆变继电器粘死 |  | 不可恢复 | To fault mode,bypass output | Check whether the inverter relay is stuck firmly or has other abnormity or not., if it is stuck,replace it. | Please get in touch with nearby EAST service branches or offices | Fault | Replace the inverter relay.
LSCR FAIL | LSCRFAIL | X23 | 23 | Rectifier SCR fault（reserved） | 整流SCR故障（未使用） |  | 不可恢复 | To fault mode,bypass output |  | Please get in touch with nearby EAST service branches or offices | Fault
CAn FAIL | CAnFAIL | X24 | 24 | CAN bus fail | CAN总线故障 |  | 不可恢复 | Guest UPS turns to fault mode,no bypass output;host UPS keeps current working mode. | Check whether parallel wire is open circuit or not. | Please get in touch with nearby EAST service branches or offices | Fault | 1)Check whether parallel wire is abnormal or not; 2)Check the parallel board and its wire connecting in the UPS; 3)Replace the control board.
ID FAIL | IDFAIL | X25 | 25 | Parallel ID incompatible | 并机时，物理地址冲突 |  | 不可恢复 | Guest UPS turns to fault mode,no bypass output;host UPS keeps current working mode. | Check the ID of every UPS,and make sure they are different. | Please get in touch with nearby EAST service branches or offices | Fault | Reset the ID of every UPS,and make sure they are different.
mOdEL F | mOdELF | X26 | 26 | Parallel model incompatible | 并机时，机型不兼容 |  | 不可恢复 | Guest UPS turns to fault mode,no bypass output;host UPS keeps current working mode. | Check the type of every UPS,if they are different,repace them. | Please get in touch with nearby EAST service branches or offices | Fault | Make sure every UPS in parallel system is the same type.
OUERTEMP | OUERTEMP | X27 | 27 | Over Temperature | 过温 |  |  | To fault mode,bypass output | Check whether environment temperature is normal or not;whether the fans are normal or not;whether the air outlet is blocked by a barrier or not. | Normal fault | Fault | 1)Check whether the fans are normal or not; 2)Check whether the air outlet is blocked by a barrier or not,make sure the distance between rear panel and wall is larger than 1 meter; 3)Check whether environment temperature is normal or not; 4)Check whether the temperature sensors on PFC board and INV board are normal or not.
OUERLOAd | OUERLOAd | X28 | 28 | Overload fault | 过载故障 |  | 不可恢复 | To fault mode, no bypass output | Remove non-critical devices to reduce the loads connected to UPS,and then Start UPS again. | Please get in touch with nearby EAST service branches or offices | Fault | 1)Check the loads capacity; 2)Check output current sampling circuit on INV board.
Sd FAIL | SdFAIL | X29 | 29 | UPS shutdown fail | 关机故障 |  | 不可恢复 | To fault mode,bypass output | Check whether SPS and control boards are normal or not. | Please get in touch with nearby EAST service branches or offices | Fault | Check whether SPS and control boards are normal or not.
SynS LOSS | SynSLOSS | X2A | 2A | Synchronize signal loss（reserved） | 同步信号异常（未使用） |  | 不可恢复 | To fault mode,bypass output |  | Please get in touch with nearby EAST service branches or offices | Fault
SynP LOSS | SynPLOSS | X2B | 2B | Synchronize pulse loss | 同步脉冲信号异常 |  | 不可恢复 | To fault mode,bypass output | Check whether parallel wires connecting is normal or not. | Please get in touch with nearby EAST service branches or offices | Fault | 1)Check whether parallel wire is abnormal or not; 2)Check the parallel board and its wire connecting in the UPS; 3)Replace the control board.
InU FAIL | InUFAIL | X2C | 2C | Inverter fail | 逆变器异常 |  | 不可恢复 | To fault mode,bypass output | Check the IGBT and its driver on INV board. | Please get in touch with nearby EAST service branches or offices | Fault | 1)Replace the control board; 2)Maintains the INV board according to maintenance manual.
WIRIng F | WIRIngF | X2D | 2D | Parallel bypass wiring is wrong | 并机时，旁路接线错误 |  | 不可恢复 | To fault mode,bypass output | Check whether bypass sequence of every parallel UPS is the same or not. | Please get in touch with nearby EAST service branches or offices | Fault | Check whether bypass sequence of every parallel UPS is the same or not.
IPSOFT F | IPSOFTF | X2E | 2E | IPSCR softstart Fail | 输入SCR软启动失败 |  | 不可恢复 | To fault mode,bypass output | Check whether mains voltage and frequency are normal or not;check whether the input SCR and its driver are normal or not. | Please get in touch with nearby EAST service branches or offices | Fault | 1)Check whether the input fuse is break or not; 2)Check whether the input SCR and its driver are normal or not; 3)Maintains the PFC board according to maintenance manual.
bAT nUM F | bATnUMF | X2F | 2F | Battery number setting is wrong | 电池节数设置错误(状态栏的单个字母“F”表示Fail) |  | 不可恢复 | To fault mode,bypass output | Check battery number setting. | Please get in touch with nearby EAST service branches or offices | Fault | Reset battery number.
A FUSE F | AFUSEF | X30 | 30 | A phase inverter Fuse break | A相逆变保险熔断 |  | 不可恢复 | To fault mode,bypass output | Check whether A phase inverter output fuse is good or not,if its bad, Replace it,and then Start UPS step by step. | Please get in touch with nearby EAST service branches or offices | Fault | Check whether A phase inverter output fuse is good or not,if its bad, Replace it,and then Start UPS step by step.
B FUSE F | BFUSEF | X31 | 31 | B phase inverter Fuse break | B相逆变保险熔断 |  | 不可恢复 | To fault mode,bypass output | Check whether B phase inverter output fuse is good or not,if its bad, Replace it,and then Start UPS step by step. | Please get in touch with nearby EAST service branches or offices | Fault | Check whether B phase inverter output fuse is good or not,if its bad, Replace it,and then Start UPS step by step.
C FUSE F | CFUSEF | X32 | 32 | C phase inverter Fuse break | C相逆变保险熔断 |  | 不可恢复 | To fault mode,bypass output | Check whether C phase inverter output fuse is good or not,if its bad, Replace it,and then Start UPS step by step. | Please get in touch with nearby EAST service branches or offices | Fault | Check whether C phase inverter output fuse is good or not,if its bad, Replace it,and then Start UPS step by step.
APFC FAIL | APFCFAIL | X33 | 33 | A phase PFC current is abnormal | A相PFC电流侦测异常 |  | 不可恢复 | To fault mode,bypass output | Check whether A phase input fuse and battery fuse are break or not. | Please get in touch with nearby EAST service branches or offices | Fault | 1)Check whether A phase input fuse and battery fuse are break or not; 2)Check A phase PFC current sampling circuit; 3)Maintains A phase PFC board according to maintenance manual.
BPFC FAIL | BPFCFAIL | X34 | 34 | B phase PFC current is abnormal | B相PFC电流侦测异常 |  | 不可恢复 | To fault mode,bypass output | Check whether B phase input fuse and battery fuse are break or not. | Please get in touch with nearby EAST service branches or offices | Fault | 1)Check whether B phase input fuse and battery fuse are break or not; 2)Check B phase PFC current sampling circuit; 4)Maintains B phase PFC board according to maintenance manual.
CPFC FAIL | CPFCFAIL | X35 | 35 | C phase PFC current is abnormal | C相PFC电流侦测异常 |  | 不可恢复 | To fault mode,bypass output | Check whether C phase input fuse and battery fuse are break or not. | Please get in touch with nearby EAST service branches or offices | Fault | 1)Check whether C phase input fuse and battery fuse are break or not; 2)Check C phase PFC current sampling circuit; 5)Maintains C phase PFC board according to maintenance manual.
nEgPOW F | nEgPOWF | X36 | 36 | Total negative power Fault | 总负功异常 |  | 不可恢复 | To fault mode,bypass output | Check whether feedback loads connected to single UPS or not;check whether feedback loads connected to parallel UPS or not,and their parallel wires are good or not. | Normal fault | Fault | Remove all the loads, and start UPS again.
FAn FAIL | FAnFAIL | X37 | 37 | Fan fail | 风扇故障 |  | 不可恢复 | To fault mode,bypass output | Check whether the fan is connected well or not; Check whether the fan is blocked and damaged or not. | Please get in touch with nearby EAST service branches or offices | Fault | 1)Check whether the fan is blocked or not; 2)Check whether the fan wire connecting and terminal are good or not; 3)Replace the control board.
EPO | EPO | X38 | 38 | emergency power shutoff | 紧急关机 |  | 不可恢复 | Bypass output or no bypass output by setting. | Check EPO wire. | Normal fault | Fault | 1)Check EPO wire; 2)Replace the control board.
OPRLY F | OPRLYF | X39 | 39 | Output relay short（reserved） | 输出继电器粘死 | 此故障未使用 | 不可恢复 |  |  |  | Fault
SET FAIL | SETFAIL | X3A | 3A | Input mode setting is wrong（reserved） | 输入方式设置错误 | 此故障未使用 | 不可恢复 |  |  |  | Fault
InU_I F | InUIF | X3B | 3B | Inverter Current is abnormal（reserved） | 逆变电流异常 | 此故障未使用 | 不可恢复 |  |  |  | Fault
保留 | 保留 | X3C | 3C | reserved | 保留 | 此故障未使用 | 不可恢复 |  |  |  | Fault
保留 | 保留 | X3D | 3D | reserved | 保留 | 此故障未使用 | 不可恢复 |  |  |  | Fault
保留 | 保留 | X3E | 3E | reserved | 保留 | 此故障未使用 | 不可恢复 |  |  |  | Fault
保留 | 保留 | X3F | 3F | reserved | 保留 | 此故障未使用 | 不可恢复 |  |  |  | Fault
以下为告警信息（现象为蜂鸣器和LED灯会告警）：
mS REUERS | mSREUERS | X40 | 40 | Mains reverse sequence | 主路相序错误(状态栏的前面两个字母“mS”表示mains) |  |  | Forbid to start UPS | Mains reverse sequence,exchange two any phase among three phase. | Normal warning | Warning
mS HIgH | mSHIgH | X41 | 41 | Mains voltage is high | 主路高压 |  |  | To battery mode | Measure whether mains voltage is normal or not. | Normal warning | Warning
P SOFT F | PSOFTF | X42 | 42 | Parallel Software version Fault | 并机时各台机器的软件版本不一致(未使用) |  |  | Forbid to start UPS | Upgrade all UPS control program,and ensure the program version is the same. | Normal warning | Warning
mS UnbAL | mSUnbAL | x43 | 43 | Mains unbalance | 主路三相电压严重不平衡 |  |  | Forbid to start UPS | Measure whether mains voltage(three phase) is normal or not. | Normal warning | Warning
mS PHASE | mSPHASE | X44 | 44 | Mains lack of phase | 主路缺相 |  |  | Forbid to start UPS | Check whether wiring is normal or not;whether input breaker is open or not;whether input fuse is open or not. | Normal warning | Warning
mSFREqAbn | mSFREqAbn | X45 | 45 | Mains frequency is abnormal | 主路频率异常（状态栏的FREq表示Frequency，Abn表示Abnormal） |  |  | To battery mode | Measure whether mains frequency is normal or not. | Normal warning | Warning
mS N LOSS | mSNLOSS | X46 | 46 | Mains neutral loss | 主路零线未接(状态栏的单个字母“N”表示Neutral) |  |  | Forbid to start UPS | Check whether neutral connecting is normal or not, whether distribution box breakers are normal or not,and make sure they are turned on. | Normal warning | Warning
mS LOSS | mSLOSS | X47 | 47 | Mains voltage is loss or Mains Wave is abnormal | 输入波形异常或主路低压 |  |  | To battery mode | Check whether mains wave is normal or not,whether mains voltage is normal or not. | Normal warning | Warning
ms bs RE | msbsRE | X48 | 48 | mains and bypass reverse sequence | 旁路和主路相序不同 |  |  | Forbid to start UPS | Check bypass and mains wiring. | Normal warning | Warning
bS REUERS | bSREUERS | X49 | 49 | Bypass reverse sequence | 旁路相序错误(状态栏的前面两个字母“bS”表示bypass) |  |  | Forbid to start UPS | Bypass reverse sequence,exchange two any phase among three phase. | Normal warning | Warning
bS HIgH | bSHIgH | X4A | 4A | Bypass voltage is high | 旁路高压 |  |  | Forbid turning to bypass mode | Check whether bypass voltage is normal or not. | Normal warning | Warning
bS E HIgH | bSEHIgH | X4B | 4B | Bypass voltage is extremely high | 旁路电压极高（状态栏的单个字母“E”表示Extremely） |  |  | Forbid turning to bypass mode | Check whether bypass voltage is normal or not. | Normal warning | Warning
保留 | 保留 | X4C | 4C | reserved | 未使用 |  |  |  |  | Normal warning | Warning
bS UnbAL | bSUnbAL | X4D | 4D | Bypass unbalance | 旁路3相电压严重不平衡(未使用) |  |  | Forbid to start UPS | Check whether bypass voltage is normal or not. | Normal warning | Warning
bS PHASE | bSPHASE | X4E | 4E | Bypass lack of phase | 旁路缺相 |  |  | Forbid to start UPS | Check whether bypass wiring is normal or not;whether bypass breaker is open or not;whether bypass fuse is open or not. | Normal warning | Warning
bSFREqAbn | bSFREqAbn | X4F | 4F | Bypass frequency is abnormal | 旁路频率异常 |  |  | Forbid turning to bypass mode | Check whether bypass frequency is normal or not. | Normal warning | Warning
bS N LOSS | bSNLOSS | X50 | 50 | Bypass neutral loss | 旁路零线未接 |  |  | Forbid to start UPS | Check bypass wiring and distribution box bypass breaker. | Normal warning | Warning
bS Loss | bSLoss | X51 | 51 | Bypass voltage is low or Bypass Wave is abnormal | 旁路低压或旁路波形异常 |  |  | Forbid turning to bypass mode | Check whether bypass wave is normal or not,whether bypass voltage is normal or not. | Normal warning | Warning
bAT LOW | bATLOW | X52 | 52 | Battery low | 电池低压 |  |  | Warning | Remove non-critical devices and charge the battery as soon as possible. | Normal warning | Warning
EOd | EOd | X53 | 53 | End Off Discharge | 电池放电终止 |  |  | Battery mode to standby mode or bypass mode\ | Charge the battery as soon as possible. | Normal warning | Warning
bAT dISC | bATdISC | X54 | 54 | Battery disconnect | 电池未接 |  |  | Shutdown charger | Connect battery and switch on battery breaker. | Normal warning | Warning
保留 | 保留 | X55 | 55 | reserved | 未使用 |  |  |  |  | Normal warning | Warning
CHgR FAIL | CHgRFAIL | X56 | 56 | Charger fail | 充电器故障 |  |  | Shutdown charger | Switch off battery breaker, remove devices connected to UPS, shutdown UPS, and replace the charger. | Normal warning | Warning
bAT HIgH | bATHIgH | X57 | 57 | Over charge | 充电器过充 |  |  | Shutdown charger | Switch off battery breaker, remove devices connected to UPS, shutdown UPS, and replace the charger. | Normal warning | Warning
INV_I F | INVIF | X58 | 58 | Inverter current is abnormal | 逆变电流侦测异常（未使用） |  |  |  |  | Normal warning | Warning
APFC FAIL | APFCFAIL | X59 | 59 | A phase PFC current is abnormal | A相PFC电流侦测异常 |  |  | A phase PFC no working | Shutdown UPS, check A phase input fuse, battery fuse and SCR. | Normal warning | Warning
BPFC FAIL | BPFCFAIL | X5A | 5A | B phase PFC current is abnormal | B相PFC电流侦测异常 |  |  | B phase PFC no working | Shutdown UPS, check B phase input fuse, battery fuse and SCR. | Normal warning | Warning
CPFC FAIL | CPFCFAIL | X5B | 5B | C phase PFC current is abnormal | C相PFC电流侦测异常 |  |  | C phase PFC no working | Shutdown UPS, check C phase input fuse, battery fuse and SCR. | Normal warning | Warning
OUER LOAd | OUERLOAd | X5C | 5C | Overload warning | UPS过载告警 |  |  | Overload time is over,to bypass mode;overload time is over in bypass mode,to fault mode,no bypass output. | Remove non-critical devices to reduce the loads connected to UPS. | Normal warning | Warning
CAn FAIL | CAnFAIL | X5D | 5D | CAN Communication fail | CAN通讯异常 |  |  | Forbid to start UPS | Check the parallel wire connecting and parallel board are abnormal or not. | Normal warning | Warning
EEPROM F | EEPROMF | X5E | 5E | EEPROM Read/Write fail | EEPROM异常 |  |  | Program judges parameters are nomal or not,if they are normal,parameters keep on,if they are abnormal,the paremeters auto reset. | Clean the warning by LCD panel or using debug software. Or shutdown UPS and startup again. | Normal warning | Warning
FAn FAIL | FAnFAIL | X5F | 5F | Fan fail | 风扇异常 |  |  | To fault mode,bypass output | Check whether the fan is connected well or not; Check whether the fan is blocked and damaged or not. | Normal warning | Warning
Ad FAIL | AdFAIL | X60 | 60 | AD sample fail | AD采样异常 |  |  | Keep in standby mode | Check all sampling circuits and replace the control board. | Normal warning | Warning
STARTUP F | STARTUPF | X61 | 61 | UPS startup fail | 开机异常 |  |  | Cancel startup | Make sure mains is normal,restart UPS again. | Normal warning | Warning
OP_U F | OPUF | X62 | 62 | Output voltage is abnormal | 输出电压侦测异常（未使用） |  |  |  | Measure whether output voltage is normal or not. | Normal warning | Warning
bAT UOL F | bATUOLF | X63 | 63 | Battery voltage is abnormal | 电池电压异常（未使用） |  |  | Forbid to start UPS | Check whether battery voltage is normal or not. | Normal warning | Warning
ECO InST | ECOInST | X64 | 64 | ECO instable | ECO不稳定 |  |  | Forbid entering into ECO mode | Clean the warning by LCD panel or using debug software. When mains and bypass are normal, set ECO enable. | Normal warning | Warning
LOAd UnST | LOAdUnST | X65 | 65 | Load unstable | 负载不稳定（未使用） |  |  | Forbid entering into inverter mode |  | Normal warning | Warning
MB EnAblE | MBEnAblE | X66 | 66 | Maintenance bypass breaker open | 维修旁路的微动开关断开 |  |  | To bypass output,forbid to start UPS | Fix the maintenance bypass baffle. | Normal warning | Warning
PAL SET F | PALSETF | X67 | 67 | Parallel Set Fail | 并机设置异常 |  |  | Forbid to start UPS | For single UPS,set PAL off; for parallel UPS,set PAL on and connect the communication wire. | Normal warning | Warning
TEMPOFTEN | TEMPOFTEN | X68 | 68 | Over Temperature often | 过温频繁 |  |  | Keep in bypass mode, no restarting. | Clean the warning by LCD panel or using debug software, or start UPS to clean the warning. (Insure to find the reason of over temperature) | Normal warning | Warning
SynP LOSS | SynPLOSS | X6A | 6A | Synchronize pulse loss | 同步脉冲信号异常 |  |  | Host and guest UPS are all warning,all keeping in current working mode. | Check the parallel wire connecting and parallel board are abnormal or not. | Normal warning | Warning
SynS LOSS | SynSLOSS | X69 | 69 | Synchronize signal loss | 同步信号异常 |  |  | Guest UPS turns to fault mode,no bypass output;host UPS keeps current working mode;forbid to restart. | Check the parallel wire connecting and parallel board are abnormal or not. | Normal warning | Warning
P BAT N F | PBATNF | X6B | 6B | Parallel Bat Num is wrong | 并机电池节数设置不一致 |  |  | Forbid to start UPS | Set battery number by LCD panel again. | Normal warning | Warning
baT Tem F | baTTemF | X6C | 6C | Battery temperature compensation is abnormal | 电池温度补偿异常（未使用） |  |  | Shutdown charger |  | Normal warning | Warning
bS InST | bSInST | X6D | 6D | Bypass instable | 旁路不稳定 |  |  | Forbid turning to bypass | Check whether bypass voltage and frequency are abnormal or not. | Normal warning | Warning
Test | Test | X6E | 6E | Test Mode | 测试模式 |  |  | Enter into test mode | You can cancel TEST MODE using debug software. | Normal warning | Warning
LOAdOFTEN | LOAdOFTEN | X6F | 6F | Overload Often | 过载频繁 |  |  | Keep in bypass mode, no restarting. | Clean the warning by LCD panel or using debug software, or start UPS to clean the warning. (Insure to find the reason of overload.) | Normal warning | Warning
保留 | 保留 | X70 | 70 | reserved | 未使用 | 未使用 | 未使用 |  |  | Normal warning | Warning
保留 | 保留 | X71 | 71 | reserved | 未使用 | 未使用 | 未使用 |  |  | Normal warning | Warning
保留 | 保留 | X72 | 72 | reserved | 未使用 | 未使用 | 未使用 |  |  | Normal warning | Warning
保留 | 保留 | X73 | 73 | reserved | 未使用 | 未使用 | 未使用 |  |  | Normal warning | Warning
保留 | 保留 | X74 | 74 | reserved | 未使用 | 未使用 | 未使用 |  |  | Normal warning | Warning
保留 | 保留 | X75 | 75 | reserved | 未使用 | 未使用 | 未使用 |  |  | Normal warning | Warning
保留 | 保留 | X76 | 76 | reserved | 未使用 | 未使用 | 未使用 |  |  | Normal warning | Warning
保留 | 保留 | X77 | 77 | reserved | 未使用 | 未使用 | 未使用 |  |  | Normal warning | Warning
保留 | 保留 | X78 | 78 | reserved | 未使用 | 未使用 | 未使用 |  |  | Normal warning | Warning
保留 | 保留 | X79 | 79 | reserved | 未使用 | 未使用 | 未使用 |  |  | Normal warning | Warning
Syn FAIL | SynFAIL | X7A | 7A | Synchronization fail | 锁相异常 | 未使用 | 未使用 |  |  | Normal warning | Warning
mS pULSE | mSpULSE | X7B | 7B | Mains pulse voltage | 主路瞬间高压（X为1时A相瞬间高压，X为2时B相瞬间高压，X为3时C相瞬间高压，X为4时两相瞬间高压,X为5时三相瞬间高压，X为0时表示告警清除） | 任意一相的电压瞬时值连续两拍大于420V？ | 未使用 |  |  | Normal warning | Warning
保留 | 保留 | X7C | 7C | reserved | 未使用 | 未使用 | 未使用 |  |  | Normal warning | Warning
保留 | 保留 | X7D | 7D | reserved | 未使用 | 未使用 | 未使用 |  |  | Normal warning | Warning
保留 | 保留 | X7E | 7E | reserved | 未使用 | 未使用 | 未使用 |  |  | Normal warning | Warning
保留 | 保留 | X7F | 7F | reserved | 未使用 | 未使用 | 未使用 |  |  | Normal warning | Warning
以下为事件信息：
|  | X80 | 80 | Bus softstart | Bus 软启动 |  |  |  |  | Normal working | Event
|  | X81 | 81 | Inverter softstart | 逆变软启动 |  |  |  |  | Normal working | Event
|  | X82 | 82 | IPSCR softstart | 输入SCR软启动 |  |  |  |  | Normal working | Event
|  | X83 | 83 | Fast IPSCR softstart | 输入SCR快速启动 |  |  |  |  | Normal working | Event
|  | X84 | 84 | UPS Off | UPS关机 |  |  |  |  | Normal working | Event
|  | X85 | 85 | UPS On | UPS开机 |  |  |  |  | Normal working | Event
|  | X86 | 86 | Charger On | 充电器开启 |  |  |  |  | Normal working | Event
|  | X87 | 87 | Charger Off | 充电器关闭 |  |  |  |  | Normal working | Event
|  | X88 | 88 | Average Charge | 充电器均充 |  |  |  |  | Normal working | Event
|  | X89 | 89 | Float Charge | 充电器浮充 |  |  |  |  | Normal working | Event
|  | X8A | 8A | Dormant Charger | 充电器休眠 |  |  |  |  | Normal working | Event
|  | X8B | 8B | Reset Charger | 充电器待机 |  |  |  |  | Normal working | Event
|  | X8C | 8C | Auto start | 自动重启 |  |  |  |  | Normal working | Event
|  | X8D | 8D | Inverter Relay Working | 逆变继电器吸合 |  |  |  |  | Normal working | Event
|  | X8E | 8E | reserved | 保留 |  |  |  |  | Normal working | Event
|  | X8F | 8F | reserved | 保留 |  |  |  |  | Normal working | Event
备注 | 备注 |  |  | 历史记录X0X（X=1-F）表示模式；LCD模式栏显示具体模式内容，最多显示6个字母。 | 历史记录X10-X3F表示故障，X是标志位，1-F表示故障发生，0表示故障清除；LCD状态栏显示具体故障内容，最多显示9个字母。 | 历史记录X40-X7F表示告警，X是标志位，1-F表示告警发生，0表示告警清除；LCD状态栏显示具体告警内容，最多显示9个字母。
/ | / |  |  | Status of charger (X=1 means charger on, X=0 means charger off) | 充电器状态（X为1时表示充电器开启，X为0时表示充电器关闭）
/ | / |  |  | Status of inverter relay(X=1 means relay on, X=0 means relay off) | 逆变继电器状态（X为1时表示继电器吸合，X为0时表示继电器断开）
/ | / |  |  | Status of output relay(X=1 means relay on, X=0 means relay off) | 输出继电器状态（同第44项）